## Table 1
TCOMM911 ERCES Design Approval
Project Name
Street Address
City State ZIP
TCOMM911 Signature
Summary of Review
1 | Statement of Purpose:
1.1 | TCOMM911 has instituted design review and approval for the following reasons: • To protect the integrity of the radio network from interference sources • To earlier identify and intercept interference sources as the result of unapproved equipment or design decisions • To better integrate radio operator approval with fire AHJ approval processes • To verify adherence to TCOMM911 technical criteria and the uplink validation process. Supplemental documentation is available at https://tcomm911.org • To reduce risk to property developers and ERCES vendors when commissioning ERCES
2 | Submittal Review
| Section | Pass/Fail Criteria | Pass, Pass with Comments, Fail | Comments
2.1 | Transmittals | All documentation must be: • Of sufficient quality and free of extraneous markings so as to be legible
• Color is permitted but must be legible in grayscale • Versioned, with date of the respective version compilation • Included • Designer qualifications • Construction floor plans • Donor Information • One-line diagram • Equipment list • Equipment cut sheets • Radio performance calculations • Coverage predictions • TCOMM911 Rebroadcast Agreement
2.2 | Designer Qualifications | • Designer's FCC GROL • Either designer's certificate of training by an approved organization or, designer's certificate issued by the manufacturer of the active RF equipment being installed
2.3 | PE certifying letter | If required.
2.4 | Construction floor plans | • Match the same orientation • Indicate version and date • Show the location with unique labels of each cable, splitter, coupler, tapper, antenna, BDA, fiber-fed remote, and donor antenna • Documentation must be legible so as to distinguish items
2.5 | Donor information | • Google Earth elevation profile between building location and elected donor site (TCOMM911 retains the right to require use of an alternate donor site) • Donor line of sight shall be unobstructed, or explanation shall be provided as to why obstructed line of sight is the best choice. • Google Earth 1/4 mile surroundings view with donor azimuth indicated • Indication on roof floor plan of proposed donor location
2.6 | One-line Diagram | • Must present the cable connection between all DAS antennas and the donor antenna, incorporating connections to external filters, splitters, directional couplers, tappers, fiber-fed remotes, the BDA, and lightning arrestor • Must present unique labels of each cable, filter, splitter, coupler, tapper, antenna, BDA, fiber-fed remote, and donor antenna
2.7 | Equipment List | ERCES equipment list shall include the following components if present: • BDA • Fiber-fed remote • Point of interface/DAS tray • Discrete fiber transceiver(s) • Coaxial cable • Donor antenna • DAS/Service antennas • Lightning arrestor • Splitters/Couplers/Tappers • External filters For each component in the equipment list, provide: • Manufacturer • Model number • Options or Licenses as appropriate • Quantity • Unit (if length of cable)
2.8 | Equipment Cut Sheets | • Manufacturer information sheets shall be provided for each item on the ERCES equipment list. • Conformance to many of the TCOMM911 technical criteria will be demonstrated through the equipment cut sheets.
2.9 | Downlink Performance Calcs | Present the following: • Table shown in the TCOMM911 Design Approval document • DL PPCH must be used to generate coverage prediction mapping for item 2.11
2.1 | Uplink Performance Calcs | Present the following: • Tables shown in the TCOMM911 Design Approval document • Arrows or clouds on coverage predictions identifying the highest and lowest UL locations • Indicate how the combination of BDA channelized AGC and dynamic receive range at the broadcast site between -75 dBm and -100 dBm will satisfy strongest- and weakest-case transmissions • Max ERP must be ≤ +37dBm per channel
2.11 | Coverage Predicitions | Present the following: • Floorplan coverage predictions for each floor and area receiving DAS coverage. • A legend for the prediction color code, including the percent of floor area receiving at least the indicated level of signal. • Show minimum signal strength of -95dBm in 95% of coverage area, and 99% of critical areas. • Any portion of the building where coverage is planned to be provided by either through-floor signal or macro coverage must be clouded and noted. Through-floor coverage notation must also describe the material composition of the floor and expected attenuation.
2.12 | TCOMM911 Rebroadcast Agreement | • Agreement must be completed and signed
3 | Summary
3.1 | Reviewing Staff
3.2 | Date of Review

## Sheet1
PASS
FAIL
Pass with Comments